{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet2"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet2","index":0,"n_rows":109,"n_cols":10,"rows_kept":109,"merged":[[0,0,0,9],[106,0,106,9],[108,0,108,6]],"flags":["formulas_cached_only"]}
["汕头大学理学院洁净实验室改造项目工程量清单"]
["序号","项目名称","规格参数","单位","数量","材料单价","人工单价","综合单价","合价","备注"]
["一","拆除及改装部分"]
[1,"原房间有关拆除","原铝扣板天花99.2m²拆除，原室内左边靠墙矮柜约10.9米长拆除，原照明灯具拆除，含垃圾清运处理","项",1]
[2,"喷淋烟感改装",null,"项",1]
[3,"洗手盆移装",null,"项",1]
[null,"小 计"]
[]
["二","围护结构部分"]
[1,"围护用岩棉彩钢板","企口型50mm,金属面板0.426mm，含结构用香槟色铝型材及玻璃胶","m²",180,{"$nulls":4},"昌隆"]
[2,"吊顶中空玻镁彩钢板","企口型50mm,金属面板0.426mm，含结构用香槟色铝型材及玻璃胶","m²",98,{"$nulls":4},"昌隆"]
[3,"彩钢板净化密闭单开门","900*2100mm(H)，带视窗","套",2,{"$nulls":4},"国标"]
[4,"彩钢板净化密闭单开门","1000*2100mm(H)，带视窗","套",1,{"$nulls":4},"国标"]
[5,"彩钢板净化密闭双开门","1500*2100mm(H)，带视窗","套",1,{"$nulls":4},"国标"]
[6,"管道井门","1000*1500mm(H)","套",1,{"$nulls":4},"国标"]
[7,"净化密闭观察窗","1800×1000mm(H)","套",1,{"$nulls":4},"国标"]
[null,"小 计"]
[]
["三","净化设备部分"]
[1,"单人双吹风淋室","箱体优质冷板喷塑；门及底板砂光不锈钢材质。外尺寸W1290*D1000*H2180；功率：1.5KW/380V；电子互锁，自动喷淋，喷淋时间：10-99s可调","台",1,{"$nulls":4},"国标"]
[2,"机械互锁传递窗","箱体优质冷板喷塑；内胆砂光不锈钢材质。窗口尺寸W600*D600*H600；机械互锁","台",1,{"$nulls":4},"国标"]
[]
["四","地板部分"]
[1,"PVC防静电地板（国产）","片材600×600×2mm（厚）","m²",92.2]
[2,"水泥自流平","铺PVC地板前基面找平","m²",92.2]
[null,"小 计"]
[]
["五","净化空调部分"]
[1,"吊装洁净风冷空调机","10HP，制冷量28KW,电加热量18KW，加湿量10kg/h，机外余压700Pa","台",1,{"$nulls":4},"雅顿/     科斯莱"]
[2,"防爆轴流风机","风量2100CMH,带防雨弯头","台",1,{"$nulls":4},"三禾/九州"]
[3,"排气扇","8吋","个",1,{"$nulls":4},"正野"]
[4,"防火调节阀","630*400，,70℃熔断","个",1,{"$nulls":4},"汇灵"]
[5,"矩形调节阀","400*320","个",3,{"$nulls":4},"汇灵"]
[6,"矩形调节阀","400*250","个",6,{"$nulls":4},"汇灵"]
[7,"矩形调节阀","320*250","个",7,{"$nulls":4},"汇灵"]
[8,"矩形调节阀","200*200","个",1,{"$nulls":4},"汇灵"]
[9,"门铰式侧回风百叶","400*600(带滤网)，喷塑","个",7,{"$nulls":4},"汇灵"]
[10,"新风板式初效","400*320","个",1,{"$nulls":4},"汇灵"]
[11,"排风防雨百叶","250*200","个",1,{"$nulls":4},"汇灵"]
[12,"不锈钢余压阀","400*200","个",1,{"$nulls":4},"国标"]
[13,"微压差计",null,"个",1,{"$nulls":4},"国产优质"]
[14,"高效送风口G15","风量1500CMH","套",6,{"$nulls":4},"国标"]
[15,"高效送风口G05","风量500CMH","套",1,{"$nulls":4},"国标"]
[16,"镀锌钢板矩形风管（空调）","δ=0.6㎜，含支吊架、法兰型钢、风管保温等","㎡",116,{"$nulls":4},"国标"]
[17,"镀锌钢板矩形风管（排风）","δ=0.6㎜，含支吊架、法兰型钢","㎡",25,{"$nulls":4},"国标"]
[18,"PVC活接球阀","DN20","个",1,{"$nulls":4},"联塑"]
[19,"加湿进水管（UPVC）","DN20","米",30,{"$nulls":4},"联塑"]
[20,"UPVC冷凝水排水管","DN32,含保温","米",10,{"$nulls":4},"联塑"]
[21,"空调机吊架","型钢制作","台",1,{"$nulls":4},"国标"]
[null,"小 计"]
[]
["六","工艺管道部分"]
[1,"316内抛光不锈钢管（氧气）","DN15，含管道配件、支吊架","米",11,{"$nulls":4},"国产优质"]
[2,"316内抛光不锈钢管（氢气）","DN15，含管道配件、支吊架","米",11,{"$nulls":4},"国产优质"]
[3,"316内抛光不锈钢管（氮气）","DN15，含管道配件、支吊架","米",11,{"$nulls":4},"国产优质"]
[4,"316内抛光不锈钢管（氩气）","DN15，含管道配件、支吊架","米",11,{"$nulls":4},"国产优质"]
[5,"管道脱脂处理",null,"项",1]
[6,"气体截止阀","DN15","个",10,{"$nulls":4},"国产优质"]
[7,"不锈钢高压金属软管","至设备6个接点","米",30,{"$nulls":4},"国产优质"]
[8,"UPVC管(真空泵排气）","DN40","米",34,{"$nulls":4},"联塑"]
[9,"UPVC管(自来水）","DN20","米",28,{"$nulls":4},"联塑"]
[10,"PVC活接球阀","DN20","个",2,{"$nulls":4},"联塑"]
[11,"不锈钢水龙头",null,"个",1,{"$nulls":4},"国产优质"]
[12,"管道试压",null,"项",1]
[null,"小 计"]
[]
["七","照明插座配电部分"]
[1,"配电箱","AL1","台",1,{"$nulls":4},"正泰"]
[2,"LED净化灯","2×16W","套",12,{"$nulls":4},"华东"]
[3,"防爆灯","LED管，1*16W，白光","套",1,{"$nulls":4},"新黎明"]
[4,"支架灯","LED管，1*16W，白光","套",1,{"$nulls":4},"国产优质"]
[5,"安全出口指示灯","带应急照明，LED灯，5W","套",5,{"$nulls":4},"拿斯特"]
[6,"双头应急灯","LED灯，5W","套",1,{"$nulls":4},"拿斯特"]
[7,"二三孔插座","10A；220V","套",19,{"$nulls":4},"公牛"]
[8,"一位单极大板开关","250V10A","个",4,{"$nulls":4},"公牛"]
[9,"二位单极大板开关","250V10A","个",1,{"$nulls":4},"公牛"]
[10,"防爆灯开关","250V10A","个",1,{"$nulls":4},"国产优质"]
[11,"铜芯电线","BVR-2.5mm2","米",500,{"$nulls":4},"南牌"]
[12,"铜芯电线","BVR-2*4+1*2.5mm2","米",120,{"$nulls":4},"南牌"]
[13,"阻燃型护线管","φ20-25","米",530,{"$nulls":4},"联塑"]
[null,"小 计"]
[]
["八","空调和设备配电部分"]
[1,"主配电柜","AP1，带电度表","台",1,{"$nulls":4},"正泰主件"]
[2,"排风机控制箱","AK1","台",1,{"$nulls":4},"正泰主件"]
[3,"电箱AP1配电"]
[4,"至空调机铜芯电缆","YJV-3*25+2*16","米",10,{"$nulls":4},"南牌"]
[5,"至2台设备电控柜铜芯电缆","YJV-3*16+2*10","米",50,{"$nulls":4},"南牌"]
[6,"至照明箱AL1电缆","YJV-4*6+1*4mm2","米",6,{"$nulls":4},"南牌"]
[7,"至排风机铜芯电线","BVR-5*2.5mm2","米",38,{"$nulls":4},"南牌"]
[8,"至蚀刻机铜芯电缆","YJV-3*10+2*6mm2","米",25,{"$nulls":4},"南牌"]
[9,"至显影机铜芯电缆","YJV-3*10+2*6mm2","米",25,{"$nulls":4},"南牌"]
[10,"至4台真空泵铜芯电线","BVR-5*2.5mm2","米",100,{"$nulls":4},"南牌"]
[11,"至风淋室铜芯电线","BVR-5*2.5mm2","米",15,{"$nulls":4},"南牌"]
[12,"线槽及辅材"]
[13,"镀锌线槽","200*100*1.0，含线槽支吊架","米",21,{"$nulls":4},"国标"]
[14,"PVC护线管","φ20-25","米",50,{"$nulls":4},"联塑"]
[15,"电缆铜接头",null,"项",1,{"$nulls":4},"国标"]
[null,"小 计"]
[]
["九","防静电接地配电部分"]
[1,"铜芯电线","BV-16mm2","米",60]
[2,"铜芯电线","BV-4mm2","米",40]
[3,"防静电接地桩",null,"项",1]
[null,"小 计"]
[null,"项目投标总价","（一～九）","元"]
["报价说明：                                                                                                                                                                                                                                                                                        1、项目投标总价已包括人工费、材料费、机械费、措施费、赶工费、税管费、保险费、利润和政府规费等一切费用；                                                                                                           2、上述工程量除特别说明外，其余为包干工程量，请各参投施工单位进行现场丈量核实；                                                                                                                                                        3、材料品牌参照本表备注品牌或国标优质同等品牌，以及“汕头大学建筑安装工程采用材料表”。       "]
["投标单位（盖章）：                                                                     "]
["法定代表人（签字或盖章）：                               日  期：2019年1月26日"]